## Slide 1: Case Studies
AMI, Distribution Automation, and Substation Automation
November 2013

## Slide 2
Avista

## Slide 3: Avista
Spokane Smart Circuits Project
  Goal: reduce outage times through faster detection and isolation of faults
  14 substations and 59 distribution feeders serving >110,000 customers
  Network connects >200 DA devices
Pullman Smart Grid Demonstration Project
  AMI: 13,000 power and 5,000 gas meters
  DA: 13 feeders and >60 DA devices (reclosers, cap banks, transformers)
  Part of the Pacific Northwest smart grid demonstration project
  Opportunity to extend use of networks for additional applications
Two smart grid projects underway

## Slide 4: Spokane Smart Circuits Project
Scope
14 substations
59 distribution feeders
>110,000 customers
Goals
Increased reliability
Reduce energy losses
Integration of distributed energy resources
Extend life of assets
Scope and goals
Source: Avista

## Slide 5: Smart grid enabling technologies
Communications
  Wireless to field devices
  Fiber to the substations
Distribution equipment
  Switches and reclosers
  Capacitor banks
  Regulators
Control software
  Remotely control and operate distribution equipment
  Continually analyze the system for optimization
Source: Avista

## Slide 6: Outage restoration example
All customers have power
Source: Avista

## Slide 7: Outage restoration example
Customers between Substation A and tie points lose power
Source: Avista

## Slide 8: Outage restoration example
Power restored from Substation A to switch nearest fault
Source: Avista

## Slide 9: Outage restoration example
Power restored from Substations B and C to switches nearest fault
Source: Avista

## Slide 10: Spokane Smart Circuits Project
Switched capacitors reduce conductor losses
Voltage optimization/CVR
Carbon reduction: 14,360 tons per year
  $50/ton to sequester
  $718,000/year
Energy efficient benefits
126V
120V
114V
126V
120V
114V
Chart: Savings 42,051 MWh per year
| Capacitors | Voltage Optimization | Reconductor
Savings (MWHr) | 4385 | 34839 | 2827

## Slide 11: Pullman Regional Demonstration Project
Enable active participation by customers through home automation/demand response
  Automated meters
  In-home control
  Home automation
Accommodate many generation and storage options
  Wind integration/control
  Battery backup
  Automated control
Workforce development via smart grid class at Washington State University
Focused on many aspects of smart grid

## Slide 12: Pullman Regional Demonstration Project
Switching
  Devices remotely operable
  Conservation voltage reduction
  Optimal switching flow
Voltage management
  Devices include voltage and current sensing
  DMS simulates loads
  Active Volt/VAR management
Itron OpenWay electric and gas meters
Five minute electric interval reads
Daily gas reads
Feeder and metering automation
Source: Avista

## Slide 13: Pullman Regional Demonstration Project
Faulted circuit indicators – enhanced fault localization
Smart transformers – transformer loading information
Enhanced automation devices
Source: Avista

## Slide 14: Pullman Regional Demonstration Project
Real-time monitoring of distribution circuit loading
Source: Avista

## Slide 15: Tropos opportunity summary
Spokane Smart Circuits Project
  450 routers
  Partner: none – Tropos direct
Pullman Regional Demonstration Project
  100 in Itron-branded routers
  100 Tropos 1410-B bridges integrated in transformers
  Partners: Itron, Howard
Potential to expand to other portions of Avista’s service area
Avista Spokane and Pullman
Notes: $84M ARRA grant from DOE; DTE matched this to make it a $168M project
Tropos network to be installed by July 2011 and replacing cellular network that is providing backhaul for 250,000 OpenWay smart meters today. Reason for replacing cellular: reliability issues. With Tropos can run multiple smart grid applications.
Rollout of phase I has started and must be completed by mid-2012

## Slide 16
Detroit Edison

## Slide 17: DTE Energy Initially AMI Backhaul – Now Expanding Applications
Customer need
  Replace/augment unreliable cellular network
ABB response
  AMI backhaul for 1,200,000 power meters
  Communications to 200+ DA devices
  Tropos added IPsec VPN capabilities to products to meet specific DTE needs
  Opportunity to leverage Tropos network for
    Smart gas meter backhaul
    Mobile utility workforce applications
Customer benefits
  High throughput, low latency network
    Average 1.25 Mbps throughput/7.4 msec latency to AMI collectors
    Average 3.16 Mbps throughput/ 6.2 msec latency to DA endpoints
  Exceeded target meter read success rate
Customer: DTE Energy
Transmission
Distribution
In Plant Communication
Smart Grids
Railways
Oil & Gas
Heavy Industries
Mines
Smart Cities
“We selected the Tropos mesh as it has the capacity and security to support AMI, distribution automation, mobile workforce automation and other smart grid applications.”
Brian Moccia AMI Technology Manager DTE Energy
Notes: DTE selected Tropos to provide backhaul for AMI after having issues with the cellular network providing reliable connectivity.
They quickly realized that Tropos could help them also deliver their DA communications effectively to over 180 devices covering 25% of their customers, and they could leverage the system for other applications including mobile workforce applications.
The product capability and flexibility impressed DTE’s project team, but our dedication to their needs have earned their trust and they consistently highlight the Tropos solution in their presentations on their project.

## Slide 18
Substation Automation Applications

## Slide 19: Wireless in substations
Wireless not generally consider to be a great fit for substations
If building a new substation, most likely going to put fiber in the ground (or cable trays)
Wireless networks serving feeders might terminate at fiber switch ports in substation but few other uses
Game changer – the need for utilities to retrofit existing substations with automation capabilities
What’s the business case?

## Slide 20: Main factor driving wireless in substations
However as utilities look to add automation to existing substations, wired connections are not as readily available as many had assumed
Going back and deploying fiber or fiber trays within existing substations is an expensive proposition
  Trenching costs
  Drilling holes in control cabinets
  Safety considerations
For substation retrofits, wireless is a great fit
Desire to avoid trenching in substation yards

## Slide 21: Example #1
Starting automate substations with SCADA (specifically voltage regulators)
Communication requirements
  Access to control panels without pulling any communications cables
  No holes drilled in regulator cabinets as this would increase both installation time and costs
  Access to controls from anywhere within the substation
    Check or change settings, update firmware and control regulators from safe distance
    Readily available monitoring, data logging, power quality, and condition-based maintenance information
  Support for proper cyber security standards
Substation automation with integrated communications

## Slide 22: Voltage regulator controller opportunity
Substation pilot architecture
Wireless bridges communicate to a Tropos wireless gateway mounted outside the control house
Gateway connects to Layer 2 switch in the control house via Ethernet
  Layer 2 switch also connects to an automation control unit
L2 switch provides optical isolation and allows other devices in substation access to wireless network and substation computer
  Protocol used is DNP3 over TCP/IP
Can also access individual controls over the wireless network
Tropos 1410 wireless bridges installed in each regulator cabinet
  Antennas were selected to provide enough signal strength when mounted inside the cabinets
  Throughput still more than 1 Mbps
  Output of radios configured so that it’s strong to operate within the substation, but is not visible outside the fence
  SSID of network is hidden
Ethernet used to connect regulator controllers and Tropos wireless bridges
~150 feet from regulators to control house
Notes: Tropos has networks aggregating close to 300,000 meters today and that number is continuing to grow as customers rollout smart metering networks.
22

## Slide 23: Example #2
Utility had gas monitors that they require readings from a few times a day
Doing lifecycle monitoring and management as lead time on replacement transformers is approximately two years
The substation itself has fiber connectivity (backhaul) but the utility stated it was too difficult and too expensive to install fiber within the substation yard
Previously each gas monitor was connected via a Sierra Wireless cellular modem
  Field communications manager wanted to reduce cellular communication costs
  For the pilot, cellular cards with a Tropos 1410 which connect to a gateway at the control house
  Still backhauling via cellular out of the substation
Cut cell modem requirement, reducing operating expenses
Substation transformer gas monitor sensors

## Slide 24: Substation wireless enables applications beyond automation
Security applications can use the wireless network to support video surveillance cameras and intrusion sensors
Transformer monitoring via the wireless network using smart transformers or gas sensors mounted near conventional transformers
Mobile workforce applications enabled by connecting field workers’ laptops, tablets and handhelds to the substation’s wireless network